Bosch Security Systems is a leading global supplier of security, safety, and communications products and systems. Protecting lives, buildings, and assets is the major aim. The product portfolio includes video security, intrusion detection, and fire detection as well as access control and management systems.

For additional information, contact:

| Americas Bosch Security Systems, Inc. 130 Perinton Parkway Fairport, New York, 14450, USA Phone: + 1 800 289 0096 Fax: +1 585 223 9180 CSI@us.bosch.com www.boschsecurity.us | Europe, Middle East, Africa Bosch Security Systems B.V. P.O. Box 80002 5600 JB Eindhoven, The Netherlands Phone: + 31 40 2577 284 Fax: +31 40 2577 330 emea.securitysystems@bosch.com www.boschsecurity.com | Asia-Pacific Robert Bosch (SEA) Pte Ltd, Security Systems 11 Bishan Street 21 Singapore 573943 Phone: +65 6571 2600 Fax: +65 6571 2698 apr.securitysystems@bosch.com www.boschsecurity.com |
| --- | --- | --- |

NDI-5513-AL-IN FLEXIDOME IP indoor 5000i 5MP IR camera

DIVISION 28 – ELECTRONIC SAFETY AND SECURITY

28 20 00 	Video Surveillance

28 21 00 	Surveillance Cameras

28 21 13	IP Cameras

Notes to Specifier:

1.  Where several alternative parameters or specifications exist, or where, the specifier has the option of inserting text, such choices are presented in <bold bracketed text>.

2.  Explanatory notes and comments are presented in italicized colored text.

FLEXIDOME IP indoor 5000i IR

- GENERAL

  - SUMMARY

    - Section includes a 5MP professional IP dome camera for indoor MP surveillance with H.265, Essential Video Analytics and integrated infrared.

## Related Requirements

      - 27 15 00 Communications Horizontal Cabling

      - 27 20 00 Data Communications

      - 28 05 00 Common Work Results for Electronic Safety and Security

      - 28 06 20 Schedules for Video Surveillance

      - 28 16 15 Access Control Interfaces to Video Surveillance

      - 28 23 00 Video Management System

      - 28 31 31.15 Intrusion Detection Interfaces to Video Surveillance

      - 28 51 15.13 Information Interfaces to Video Surveillance Systems

  - REFERENCES

    - Abbreviations

      - AI – Artificial Intelligence

      - ARP – Address Resolution Protocol

      - DHCP - Dynamic Host Configuration Protocol

      - DNS - Domain Name Server

      - DDNS – Dynamic DNS

      - DORI - Detect, Observe, Recognize, Identify

      - fps - frames per second

      - HEVC – High Efficiency Video Coding

      - HTTPS – Secure Hypertext Transfer Protocol

      - ICMP - Internet Control Message Protocol

      - IP - Internet Protocol

      - IR – InfraRed

      - JPEG - Joint Photographic Experts Group

      - mDNS – Multicast DNS

      - MP - Megapixel

      - MJPEG - Motion JPEG

      - NTP - Network Time Protocol

      - PKI - Public Key Infrastructure

      - PoE - Power over Ethernet

      - RTCP – Real-Time Control Protocol

      - RTP - Real-Time Transport Protocol

      - RTSP - Real-Time Streaming Protocol

      - TCP - Transmission Control Protocol

      - TPM - Trusted Platform Module

      - TLS – Transport Layer Security

      - UDP - User Datagram Protocol

    - Reference Standards

      - Australia and New Zealand Standards

        - AS/NZS CISPR 22 Information technology equipment - Radio disturbance characteristics - Limits and methods of measurement

        - Conforms to C-tick standards

      - Canadian Standards Association (CSA)

        - CAN/CSA C22.2 No. 62368-1-14

        - Conforms to cUL standards

      - European Norm

        - EN 50121-4:2006 Railway Applications - Electromagnetic Compatibility - Part 4: Emission And Immunity Of The Signaling And Telecommunications Apparatus

        - EMC directive 2004/108/EC

        - EN 50130-4:1995+A1:1998+A2:2003 (CE) Alarm Systems, Part 4 – Electromagnetic Compatibility – Product Family Standard: Immunity Requirements for Components of Fire, Intruder and Social Alarm Systems.

        - EN 50130-5: Alarm Systems, Part 5 – Environmental Test Methods (corresponds with VDE 0830 parts 1-5)

        - EN 50132-5-2: Alarm systems - CCTV surveillance systems for use in security applications - Part 5-2: IP Video Transmission Protocols

        - EN 55032, Class B – Information Technology Equipment – Radio Disturbance Characteristics – Limits and Methods of Measurement for Emission

        - EN 55024 Information technology equipment. Immunity characteristics. Limits and methods of measurement

        - EN 62368-1

        - CE Declaration of Conformity

        - CB scheme

      - Federal Communications Commission (FCC) (www.fcc.gov)

        - FCC CFR 47 part 15; subpart B, Class B Digital Devices

      - Industry Canada

        - ICES-003 Class B Spectrum Management and Telecommunications Policy Interference-Causing Equipment Standard

      - International Electrotechnical Commission (IEC):

        - IEC 62676-2-3: Video surveillance systems for use in security applications – Part 2-3: Video transmission protocols – IP interoperability implementation based on WEB services.

        - IEC 62471 (IR lighting): Photobiological safety of lamps and lamp systems.

      - International Organization for Standardization (ISO)

        - 9001: Quality System

      - Underwriters Laboratories, Inc. (UL) (www.ul.com)

        - UL 60950-1 UL Standard for Safety of Information Technology Equipment.

      - Voluntary Control Council for Interference (VCCI)

        - VCCI-CISPR 32

      - Other

        - RoHS EU, 2011/65/EU and 2015/863/EU

        - WEEE EU, 2012/19/EU

  - SUBMITTALS

    - Informational Submittals

      - Product Data

        - Manufacturer’s printed or electronic data sheets

        - Manufacturer’s installation and operation manuals

        - Warranty documentation

      - Shop Drawings

      - Cyber hardening guidance

    - Closeout Submittals

      - Final listing of devices and settings

      - System test results

      - Statement of compliance with Manufacturer Cyber Hardening Guidelines

  - QUALIFICATIONS

    - Installers shall be certified, trained and authorized by the Manufacturer to install, integrate, test, and commission the system.

  - DELIVERY, STORAGE AND HANDLING

    - Deliver the camera in the manufacturer’s original, unopened, undamaged container with identification labels intact.

    - Store the camera in a temperature environment protected from mechanical and environmental conditions as designated by the manufacturer.

  - WARRANTY AND SUPPORT

    - Manufacturer shall provide a limited 3-year warranty for the product to be free of defects in material and workmanship, with option to extend the warranty to 5 years.

END OF SECTION

- PRODUCTS

  - EQUIPMENT

    - Manufacturer: 	Bosch Security Systems, Inc.

130 Perinton Parkway

Fairport, New York, 14450

USA

Phone: +1 800 289 0096

Fax: +1 585 223 9180

Email: technical.support@us.bosch.com

    - Product Model:	NDI-5513-AL-IN

  - GENERAL DESCRIPTION

    - The fixed-dome camera shall be a 5MP professional IP dome camera for indoor MP surveillance with H.265, Essential Video Analytics and integrated infrared.

    - The dome camera shall possess the following primary characteristics:

      - Complete indoor network video surveillance system inside a dome camera.

      - 5MP resolution.

      - Built-in active infrared illuminator.

      - Built-in Essential Video Analytics to trigger relevant alerts and quickly retrieve data.

      - High Dynamic Range (HDR) to see details in bright and dark areas simultaneously.

      - Intelligent Dynamic Noise Reduction (iDNR) technology.

      - Intelligent streaming technology for reduced bitrates

      - H.264 and H.265 encoding

      - Automatic varifocal 3 to 9 mm, DC Iris fixed board-mounted lens.

      - True day/night function.

      - Quad-streaming IP video

      - Micro SDHC/SDXC card slot for edge recording up to 2 TB.

      - ONVIF conformant.

      - +12 VDC, +24 VAC and Power over Ethernet (IEEE 802.3af compliant).

  - ADDITIONAL VIDEO/CAMERA SPECIFICATIONS

    - Imaging Requirements:

      - The camera shall offer a 1/2.9-inch CMOS image sensor.

      - The camera shall produce a video resolution of 3072x1728 pixels (MP 5MP) at 30 fps with a 16:9 aspect ratio.

      - The camera shall produce a video resolution of 2688x1512 pixels (MP 4MP) at 30 fps with a 16:9 aspect ratio.

      - The camera shall produce a video resolution of 2304x1296 pixels (MP 3MP) at 30 fps with a 16:9 aspect ratio.

      - The camera shall produce a resolution of 1920 x 1080 pixels (HD 1080p) at 30 fps with a 16:9 aspect ratio.

      - The camera shall offer an upright mode

      - The camera shall be fitted with a board-mounted fixed varifocal 3 to 9 mm, DC Iris, F1.3 lens with a lens view angle of:

      - 93° - 34° (Horizontal)

      - 49° - 19° (Vertical)

      - The camera shall have a wide dynamic range of 120 dB HDR.

      - The camera shall have high sensitivity color (0.24 lx) and in monochrome (0.03 lx). The camera shall offer a minimum sensitivity of 0.0 lx in IR mode.

      - The camera automatic electronic shutter shall offer a shutter speed of 1/30 (1/25) to 1/15000.

      - The camera shall be capable of capturing and storing images using the following compression standards:

        - H.265 MP

        - H.264 MP

        - M-JPEG

    - Recording and Storage Management

      - The camera shall support iSCSI devices to allow video stream to be recorded directly to an iSCSI RAID array.

      - The camera shall support iSCSI storage targets to enable the camera to function as a conventional DVR.

      - The camera shall have an SD card slot that uses standard, off-the-shelf SD cards for local storage (up to 2TB).

      - The local storage feature shall be capable of storage for Automatic Network Replenishment (ANR).

      - Local Recording: Continuous recording, ring recording, alarm/events/schedule recording.

    - Alarm Handling Features:

      - The camera shall provide the capability on alarm to display up to a 31 character, programmable alarm message.

      - The camera shall provide email alarm messaging with optional JPEG posting.

    - Embedded Video Content Analysis

      - The camera shall be VCA enabled.

      - The camera shall be capable of processing and analyzing video within the camera itself, with no extra hardware required.

      - The camera shall be capable of detecting and sending alarms for abnormal events.

      - The camera shall allow users to set up to 10 separate profiles and switch profiles based on a day/night or holiday schedules.

      - The camera shall offer Essential Video Analytics that uses an Intelligent tracker to follow objects within the defined regions of interest.

    - Audio

      - The camera shall have line in and line out jack connectors for two-way, full duplex audio communication with audio compression AAC, G.711, L16 (live and recording).

    - Night Vision (Infrared)

      - The camera shall have a 10 LED high efficiency array (850 nm) for effective night vision up to 30 m (98 ft).

    - Control

      - The camera shall be configured via a web browser or PC surveillance software.

    - Connectors

      - The camera shall have one RJ-45 for Ethernet.

      - The camera shall have one analog video out BNC connector for installation only.

      - The camera shall have short or DC 5V activation alarm input.

      - The camera shall have one relay out (input rating maximum 1 A, 24 VAC/VDC).

      - The camera shall have one line in jack connector for audio input.

      - The camera shall have one line out jack connector for audio output

    - Access Security

      - The camera shall offer three levels of password protection.

      - The camera shall support 802.1x authentication using a RADIUS (Remote Authentication Dial In User Service) server.

      - The camera shall store an SSL certificate for use with HTTPS.

  - NETWORK

    - The camera shall provide direct network connection using H.265, H.264 and M-JPEG compression and bandwidth throttling to efficiently manage bandwidth and storage requirements while delivering outstanding image quality.

    - The camera shall allow full camera control and configuration capabilities over the network.

    - The camera shall deliver video, at rates up to 30 images per second, via TCP/IP over a 10/100 Base-T, auto-sensing, half/full duplex, RJ45 Ethernet connection.

    - The camera shall support AutoMDIX.

    - The camera shall conform to the ONVIF Profile S and G standard.

    - The camera shall conform to protocols: IPv4, IPv6, UDP, TCP, HTTP, HTTPS, RTP/RTCP, IGMP V2/V3, ICMP, ICMPv6, RTSP, FTP, Telnet, ARP, DHCP, SNTP, SNMP (V1, MIB II), 802.1x, DNS, DNSv6, DDNS, SMTP, iSCSI, UPnP (SSDP), DiffServ (QoS), LLDP, SOAP, Dropbox, CHAP, Digest Authentication.

  - ELECTRICAL

    - The camera shall accept either +12 VDC, +24 VAC or Power over Ethernet (48 VDC nominal).

    - The camera shall conform to the IEEE 802.3af (802.3at Type 1) compliant Power over Ethernet network. Power level: Class 3.

    - The camera shall consume 7 W (max.).

  - MECHANICAL AND ENVIRONMENTAL

    - The camera dimensions shall be:

      - Diameter 135 mm (5.32 in.)

      - Height 102 mm (4 in.).

    - The camera weight shall be 450 g (0.99 lb) approx.

    - The camera shall have 3-axis adjustment (pan/tilt/rotation), plus zoom.

    - The camera color is RAL 9003 and RAL 9017.

    - The camera shall operate in a -20°C to +50°C (-4°F to +122°F) temperature range.

    - The camera can be stored in a -30°C to +70°C (-22°F to +158°F) temperature range.

    - The camera can be operated/stored in 0% to 90% relative humidity (non-condensing).

  - ACCESSORIES

    - NDA-5031-PIP Interface plate to mount a camera to a pendant or pipe, white; for indoor use.

    - NDA-U-WMT Universal wall mount for dome cameras, white

    - NDA-U-PMT Universal pipe mount for dome cameras, 31 cm, white

    - NDA-U-PSMB Surface mount box (SMB) for wall mount or pipe mount.

    - NDA-U-PMAS Universal pole mount adapter, white; small.

    - NDA-FMT-DOME In-ceiling flush mounting kit for dome cameras (Ø157 mm).

END OF SECTION

- EXECUTION

  - INSTALLERS

    - Contractor personnel shall comply with all applicable state and local licensing requirements.

  - PREPARATION

    - The network design and configuration shall be verified for compatibility and performance with the camera(s).

    - Network configuration shall be tested and qualified by the Contractor prior to camera installation.

    - Before permanent installation of the system, the Contractor shall test the system in conditions simulating the final installed environment.

  - INSTALLATION

    - The contractor shall follow all Manufacturer-published guidance on proper installation and configuration of the installed cameras.

    - The Contractor shall test the system in conditions simulating the final installed environment

    - Reports:

      - System test results

      - System network addressing and device settings

  - STORAGE

    - Products shall be stored in an environment where temperature and humidity are in the range specified by the Manufacturer.

END OF SECTION

202410231055